FORBES SAFETY SOLUTIONS

JOB HAZARD ANALYSIS

Battery Energy Storage System (BESS) Maintenance

Document No: FSS-JHA-047

Regulatory References: NFPA 855 (Energy Storage Systems), 29 CFR 1910.269, NFPA 70E, UL 9540

PROJECT INFORMATION

| Project Name: |  | Date: |  |
| --- | --- | --- | --- |
| Location: |  | JHA Number: |  |
| Supervisor: |  | Permit Required: | ☐ Yes ☐ No |
| Work Description: | Battery Energy Storage System (BESS) Maintenance | Revision: | 0 |

JOB HAZARD ANALYSIS

| Task Step | Hazard | Risk Level (H/M/L) | Control Measures |
| --- | --- | --- | --- |
| 1. System Isolation and LOTO | Electrical shock (600V+ DC) Arc flash (high energy DC) Stranded energy — batteries remain energized even after isolation | H H H | Follow site-specific LOTO procedure; use Group LOTO for multiple workers Perform arc flash study; wear PPE per NFPA 70E incident energy calculation Verify zero energy state at each work point with CAT IV rated meter; batteries cannot be fully de-energized — maintain electrical safe work practices at all times |
| 2. Enclosure Access and Environmental Monitoring | Oxygen depletion in enclosed space Toxic gas exposure (HF, HCN from thermal event) Heat exposure inside enclosure | H H M | Continuous atmospheric monitoring with 4-gas detector (O2, LEL, CO, H2S); add HF monitor for lithium-ion systems Verify ventilation system is operational before entry; establish evacuation alarm at 1 ppm HF Monitor temperature inside enclosure; ensure HVAC is functional; provide cooling PPE if needed |
| 3. Battery Module Inspection | Electrical shock from module terminals Thermal runaway — battery fire with toxic gas Electrolyte exposure (skin/eye burns) | H H H | Wear voltage-rated gloves (Class 0 minimum); use insulated tools only; never bridge terminals Use thermal imaging to inspect modules before contact; identify swollen/damaged cells; do NOT disturb suspect modules — evacuate and contact manufacturer Wear chemical splash goggles and face shield; have spill kit with neutralizing agent; emergency eyewash within 10 seconds of travel |
| 4. DC Bus Work and Connections | DC arc flash (extreme energy — does not self-extinguish) Electrical shock (600V+ DC) Dropped tools creating short circuits | H H H | Perform detailed arc flash risk assessment for DC systems; DC arcs do NOT cross zero — use DC-rated PPE and clearing devices Verify isolation; use insulated tools; maintain safe approach boundaries Use tool tethers; remove all metallic jewelry; cover exposed bus bars with insulating blankets |
| 5. Thermal Management System Service | Refrigerant exposure Electrical contact with HVAC components Working in confined areas | M M M | EPA Section 608 certified technicians only; use refrigerant leak detectors; ensure ventilation LOTO HVAC electrical feeds; verify de-energized before service Follow confined space entry procedures if applicable; maintain communication with attendant |
| 6. Re-Energization and System Verification | Arc flash during energization Unexpected fault current Thermal event during startup | H H M | Clear all personnel from arc flash boundaries; only qualified operators energize; close disconnects remotely if possible Verify all connections torqued to specification; remove all tools and temporary grounds before energization Monitor BMS for cell voltage/temperature anomalies during ramp-up; have fire suppression system armed and verified |

REQUIRED PERSONAL PROTECTIVE EQUIPMENT (PPE)

• Arc-rated clothing per NFPA 70E arc flash study (often 40+ cal/cm² for BESS)

• Voltage-rated gloves (Class 0 minimum, 1000V DC) with leather protectors

• Arc-rated face shield and balaclava

• Safety glasses (ANSI Z87.1) under face shield

• Chemical splash goggles for electrolyte exposure risk

• Steel-toe/composite-toe EH-rated boots (ASTM F2413)

• 4-gas atmospheric monitor (O2, LEL, CO, H2S) + HF monitor

• Self-contained breathing apparatus (SCBA) staged at entry point for emergency

• Cut-resistant gloves for non-electrical tasks

• High-visibility vest when working in traffic areas

ADDITIONAL SAFETY REQUIREMENTS

• BESS systems contain stranded energy — batteries CANNOT be fully de-energized; treat all components as energized at all times

• Only manufacturer-trained and qualified electrical workers shall perform BESS maintenance

• Battery Management System (BMS) alarms must be reviewed before any enclosure entry

• Thermal imaging scan required before physical contact with any battery module

• Fire suppression system must be verified operational before maintenance begins

• Coordinate with utility/grid operator for system isolation; verify no remote energization capability

• Emergency response plan specific to thermal runaway must be reviewed with all workers before each shift

EMERGENCY PROCEDURES

• THERMAL RUNAWAY RESPONSE: Evacuate immediately; do NOT attempt to fight lithium-ion battery fire with water unless system is specifically designed for it; call 911; notify utility/system operator

• For toxic gas exposure (HF/HCN): Move to fresh air immediately; call 911; apply calcium gluconate gel to any skin exposure; do NOT induce vomiting

• For electrical shock: De-energize source if safe; do NOT touch victim in contact with energized equipment; call 911; begin CPR/AED if trained

• For arc flash burns: Remove from source; cool burns with water; do NOT remove melted clothing; call 911

• Emergency shutdown procedure posted at: ____________________

• Fire suppression system activation: ____________________

• First aid kit, AED, and SCBA located at: ____________________

• Nearest hospital/emergency room: ____________________

• Manufacturer emergency hotline: ____________________

WORKER SIGN-OFF

By signing below, I acknowledge that I have reviewed and understand this Job Hazard Analysis, the associated hazards, and the required control measures for this work activity.

| # | Print Name | Signature | Date | Company/Trade |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |

REVIEW & APPROVAL

| Role | Name / Signature | Date | Next Review Date |
| --- | --- | --- | --- |
| Prepared By |  |  |  |
| Reviewed By |  |  |  |
| Approved By |  |  |  |
| Site Safety Manager |  |  |  |

DISCLAIMER: This JHA is a template provided by Forbes Safety Solutions for general guidance. It must be reviewed, customized, and approved by a qualified safety professional before use on any specific project. Site-specific conditions may require additional hazard controls not listed herein.