FORBES SAFETY SOLUTIONS

JOB HAZARD ANALYSIS

| JHA INFORMATION |  |  |  |
| --- | --- | --- | --- |
| JHA Title: | Overhead Power Line Work | JHA Number: | FSS-JHA-026 |
| Project Name: |  | Date: |  |
| Location: |  | Revision: | 0 |
| Regulatory References: | 29 CFR 1926.1408 (Power Line Safety — Equipment Operations); 29 CFR 1910.269 (Electric Power Generation, Transmission & Distribution); NESC (National Electrical Safety Code) |  |  |
| Prepared By: |  | Approved By: |  |
| Competent Person: |  | Supervisor: |  |

JOB HAZARD ANALYSIS — TASK BREAKDOWN

| Task Step | Hazard | Risk Level (H/M/L) | Control Measures |
| --- | --- | --- | --- |
| 1. Pre-Work Planning & Utility Notification | • Unknown energized lines • Incorrect voltage identification • Inadequate clearance planning • Failure to notify utility owner | H | • Contact utility owner to identify all overhead lines and voltages • Obtain and review as-built drawings of line locations • Conduct pre-job safety briefing with all crew members • Develop written work plan specifying minimum approach distances (MAD) • Verify utility has been notified per 29 CFR 1926.1408 • Assign qualified electrical worker as crew lead |
| 2. Establishing Minimum Approach Distances | • Electrocution from insufficient clearance • Arc flash exposure • Induced voltage on equipment • Misjudged distances | H | • Reference OSHA Table A (29 CFR 1926.1408) for MAD by voltage • Post MAD signage at work area boundaries • Use non-conductive measuring devices to verify distances • Install visible warning barriers (cones, flagging, barricades) • Designate a dedicated spotter for all equipment movement • Brief all personnel on MAD requirements — no exceptions |
| 3. Equipment Setup & Grounding | • Electrical contact during setup • Inadequate grounding • Equipment tip-over on uneven terrain • Ground faults | H | • Set up equipment outside MAD zone; use outrigger pads on firm ground • Install protective grounds per utility requirements • Use ground-fault circuit interrupters on all portable tools • Verify continuity of grounding system before work begins • Ensure aerial lifts have insulated booms rated for voltage present • Conduct equipment pre-use inspection per manufacturer specs |
| 4. Conductor Work (De-Energized or Hot Stick) | • Electrocution / arc flash • Falls from structures/poles • Induced voltage from adjacent energized lines • Tool drop strikes | H | • Confirm lockout/tagout and test-before-touch on de-energized circuits • Use insulated hot-stick tools rated for voltage class • Wear arc-rated FR clothing meeting NFPA 70E requirements • Install personal grounds at worksite bracket • Use 100% tie-off fall protection on poles/structures • Employ tool lanyards to prevent dropped objects • Maintain communication with ground crew at all times |
| 5. Re-Energization & Testing | • Premature energization • Arc flash during switching • Personnel in danger zone • Residual stored energy | H | • Remove all grounds and protective devices in reverse order • Verify all personnel clear of MAD zone before re-energization • Coordinate with utility control center for switching sequence • Use proper switching PPE (arc flash suit per incident energy calc) • Perform step-and-touch voltage testing after energization • Document all switching operations in job log |
| 6. Site Restoration | • Residual energized components • Trip/fall hazards from equipment • Incomplete cleanup • Public access to hazard area | M | • Verify all circuits are properly energized or de-energized per plan • Remove all barriers, signs, grounds, and temporary equipment • Inspect work area for debris, tools, and hardware left behind • Restore public barriers and warning signs as needed • Conduct post-job debrief with crew — document lessons learned • File completed JHA with project safety records |

REQUIRED PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Required | Specification / ANSI Standard | Condition / Notes |
| --- | --- | --- |
| Hard Hat (Class E — Electrical) | ANSI/ISEA Z89.1, Class E (20kV rated) | Inspect before each use; replace if damaged |
| Arc-Rated FR Clothing | NFPA 70E; ASTM F1506 | Cal rating must meet or exceed incident energy |
| Insulated Rubber Gloves w/ Leather Protectors | ASTM D120; OSHA 1910.137 | Class matched to voltage; test per schedule |
| Safety Glasses / Arc-Rated Face Shield | ANSI/ISEA Z87.1+ | Arc-rated face shield for switching operations |
| Dielectric Safety Footwear | ASTM F2413 (EH rated) | Electrical hazard rated; inspect soles for damage |
| Fall Protection Harness & Lanyard | ANSI/ASSP Z359.1; ANSI Z359.13 | 100% tie-off required above 4 ft |
| High-Visibility Vest | ANSI/ISEA 107, Class 2 minimum | Required in all roadway/traffic areas |
| Hearing Protection | ANSI S3.19 / S12.6 (NRR ≥ 25 dB) | Required during loud operations |

EMERGENCY PROCEDURES

Electrical Contact / Electrocution:

• DO NOT touch the victim if still in contact with energized source

• Call 911 immediately and request utility emergency response

• De-energize the circuit if safe to do so (utility switching)

• If victim is clear, begin CPR/AED — electrical injuries require cardiac monitoring

• Treat for burns — cover with sterile dressings, do not apply ointments

• All electrical contact incidents require hospital evaluation regardless of apparent severity

Arc Flash Burn:

• Remove victim from hazard zone to safe area

• Cool burns with clean water — do not remove adhered clothing

• Cover burns with sterile, non-adherent dressings

• Call 911 for burns involving face, airway, hands, or large body area

• Monitor for shock symptoms and keep victim warm

Fall from Height:

• Call 911 immediately — do not move victim unless in immediate danger

• Stabilize head and neck — assume spinal injury until cleared

• Control bleeding with direct pressure

• Monitor breathing and circulation; provide CPR if needed

• Activate site emergency plan and notify project management

Emergency Contact Information:

• Emergency Services: 911

• Utility Emergency Dispatch: [Insert Local Utility Number]

• Site Safety Manager: [Insert Name & Phone]

• Nearest Hospital: [Insert Name, Address & Phone]

• Poison Control: 1-800-222-1222

WORKER SIGN-OFF — I HAVE READ AND UNDERSTAND THIS JHA

| # | Print Name | Signature | Company / Trade | Date |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |

REVIEW & APPROVAL

| Role | Name / Signature | Date | Initials |
| --- | --- | --- | --- |
| Prepared By (Author) |  |  |  |
| Reviewed By (Safety Manager) |  |  |  |
| Approved By (Project Manager) |  |  |  |
| Client / Owner Rep |  |  |  |

This JHA must be reviewed and updated whenever job conditions change, after any incident, or at minimum annually.