FORBES SAFETY SOLUTIONS

Compressed Gas
Cylinder Safety Program

Safe Handling, Storage & Use of Compressed Gas Cylinders

Prepared for:

[COMPANY NAME]

Reference Standards:

29 CFR 1926.350 | 29 CFR 1910.101 | CGA P-1

Date: [DATE]  |  Revision: [REV NUMBER]

# Table of Contents

# 1. Purpose

This Compressed Gas Cylinder Safety Program establishes requirements for the safe handling, storage, transportation, and use of compressed gas cylinders at [COMPANY NAME] in compliance with OSHA standards 29 CFR 1926.350 (Gas Welding and Cutting), 29 CFR 1910.101, and Compressed Gas Association (CGA) Pamphlet P-1.

Compressed gas cylinders present serious hazards including high-pressure release, asphyxiation, fire, explosion, and toxic exposure. This program ensures these hazards are controlled through proper procedures and training.

# 2. Scope

This program applies to all [COMPANY NAME] employees, contractors, and subcontractors who handle, store, transport, or use compressed gas cylinders including but not limited to:

- Oxygen, acetylene, argon, nitrogen, helium, CO2

- Propane, hydrogen, natural gas

- Specialty gases (calibration gases, medical gases)

- Compressed air cylinders

# 3. Responsibilities

## 3.1 Management

- Provide adequate storage facilities and handling equipment

- Ensure employees are trained before working with compressed gases

- Fund cylinder inspection, maintenance, and replacement

## 3.2 Safety Manager

- Develop and maintain this program

- Conduct training on compressed gas cylinder safety

- Perform periodic inspections of cylinder storage and use areas

- Maintain safety data sheets (SDS) for all compressed gases

## 3.3 Supervisors

- Enforce cylinder safety requirements in their work areas

- Ensure proper storage, handling, and use procedures are followed

- Remove unsafe cylinders from service

## 3.4 Employees

- Follow all procedures in this program

- Inspect cylinders before use

- Report damaged, leaking, or unidentified cylinders immediately

- Complete required training

# 4. Cylinder Identification

## 4.1 Labeling Requirements

Positive identification of the gas contents is essential before use. The following identification methods shall be used:

- Read the label: The cylinder label or stenciled name is the ONLY reliable method of identifying contents

- Check the SDS: Verify the safety data sheet matches the cylinder contents

- DOT markings: Verify Department of Transportation markings on the cylinder shoulder

## 4.2 Color Coding Warning

IMPORTANT: Color coding of cylinders is NOT a reliable method of identification. Color codes vary between manufacturers and are not standardized across the industry. NEVER rely solely on cylinder color to identify contents.

- Always read the label or stencil on the cylinder

- If a label is missing, illegible, or the contents are uncertain, do NOT use the cylinder

- Tag unidentified cylinders as "Contents Unknown" and return to the supplier

- Never deface, remove, or alter cylinder labels or markings

# 5. Storage Requirements

## 5.1 General Storage Rules

- Store cylinders upright (vertical) and secured to prevent falling

- Chain, strap, or otherwise restrain cylinders to a wall, rack, or other stable structure

- Valve protection caps must be in place when cylinders are not in active use

- Store in well-ventilated areas, away from elevators, stairs, and gangways

- Protect from extreme heat, direct sunlight, and corrosive environments

- Keep away from electrical circuits, open flames, and ignition sources

- Post "No Smoking" signs in all cylinder storage areas

## 5.2 Separation of Fuel and Oxidizer Gases

Fuel gases (acetylene, propane, hydrogen) and oxidizers (oxygen) must be separated during storage:

- Minimum 20-foot separation between fuel gas cylinders and oxygen cylinders, OR

- 5-foot-high noncombustible barrier with a fire-resistance rating of at least one-half hour between fuel and oxidizer storage

This requirement applies per 29 CFR 1926.350(a)(10) and CGA P-1.

## 5.3 Storage Area Organization

- Separate full cylinders from empty cylinders

- Label storage areas clearly: "FULL," "EMPTY," "IN USE"

- Use "first in, first out" (FIFO) rotation for cylinder inventory

- Do not store cylinders near exits or in locations that would block emergency egress

- Flammable gas storage rooms shall meet NFPA requirements for ventilation and electrical classification

# 6. Handling and Transport

## 6.1 Moving Cylinders

- Always use a suitable hand truck, cart, or cylinder trolley designed for cylinder transport

- Secure cylinders to the cart during transport

- Valve protection caps must be in place during transport

- Never drag, slide, or roll cylinders on their side

- Never drop cylinders or allow them to strike each other violently

- Never lift cylinders by the valve or valve protection cap

- Use a cradle, sling board, or pallet when hoisting cylinders by crane; never use a choker sling or electromagnet

## 6.2 Vehicle Transport

- Secure cylinders upright in a ventilated vehicle

- Do not transport in enclosed vehicle passenger compartments

- Keep valve protection caps in place

- Do not leave cylinders unattended in direct sunlight in a closed vehicle

- Follow DOT transportation regulations for quantities exceeding exempt amounts

# 7. Regulator Use

Regulators reduce the high cylinder pressure to a safe working pressure. Proper use is critical:

- Use only regulators and fittings designed for the specific gas and cylinder type

- Never use oil, grease, or lubricants on regulators, valves, or fittings (especially oxygen)

- Inspect regulator connections for damage before attaching to the cylinder

- Open cylinder valves slowly — "crack" the valve slightly before attaching the regulator to clear debris (except with acetylene or flammable gas in a confined area)

- Stand to the side of the regulator when opening the cylinder valve

- After attaching the regulator, check connections for leaks using approved leak-detection solution

- Never use Teflon tape on CGA connections (they are designed for metal-to-metal seal)

- Release pressure from regulators when not in use

# 8. Leak Testing

Test all connections for leaks after assembly using approved leak detection methods:

- Use a commercially available leak-detection solution (soapy water solution is acceptable)

- Apply solution to all connections; look for bubbles

- NEVER use a flame to check for leaks

- If a leak is detected at the valve, close the valve and attempt to tighten the packing nut gently

- If a leak cannot be stopped, move the cylinder to a well-ventilated area (outdoors if possible), tag it, and notify the supplier

- Evacuate the area if a large or uncontrollable leak occurs; contact emergency services

# 9. Prohibited Practices

The following practices are strictly prohibited:

- Using cylinders as rollers, supports, or for any purpose other than containing gas

- Dropping cylinders or allowing them to fall

- Heating cylinders to increase discharge pressure (using open flame, electric heat, steam)

- Tampering with safety relief devices

- Refilling cylinders — only authorized suppliers may refill

- Mixing gases in cylinders

- Using damaged, dented, corroded, or leaking cylinders

- Storing cylinders without valve protection caps when not connected to a system

- Using adapters to force incorrect regulators onto cylinders

- Using cylinders with unknown or unreadable contents

- Striking an arc on a cylinder

# 10. Acetylene-Specific Requirements

Acetylene presents unique hazards and requires special precautions per 29 CFR 1926.350(a) and CGA Pamphlet G-1:

- Never exceed 15 psi gauge pressure — acetylene becomes unstable and potentially explosive above 15 psig (approximately 29.4 psia). Regulators must be set to ensure working pressure stays below this limit.

- Always open acetylene cylinder valves slowly — no more than one and one-half turns

- Keep the wrench on the valve stem during use for quick shutoff in emergencies

- Do not use acetylene from a cylinder in a horizontal position — allow an upright cylinder that has been lying on its side to stand upright for a minimum of 30 minutes before use to allow the acetone to settle

- Acetylene cylinders contain porous mass and acetone — rough handling can damage the interior mass, creating voids where acetylene can decompose

- If an acetylene cylinder has been exposed to fire or excessive heat, evacuate the area (minimum 300 feet), call the fire department, and keep the cylinder cool with water if it can be done safely from a distance

# 11. Empty Cylinder Management

- Mark or tag empty cylinders clearly as "EMPTY" or "MT"

- Close the valve and replace the valve protection cap

- Store empty cylinders separately from full cylinders

- Return empty cylinders to the supplier promptly

- Treat "empty" cylinders with the same care as full cylinders — they still contain residual pressure and gas

- Never completely empty a cylinder — leave a slight positive pressure (25 psi minimum) to prevent contamination

# 12. Training

All employees who handle, transport, store, or use compressed gas cylinders shall be trained on:

- Hazards of compressed gases (pressure, flammability, toxicity, asphyxiation, reactivity)

- Proper cylinder identification (labeling, NOT color coding)

- Storage requirements (upright, secured, separated by type)

- Safe handling and transport procedures

- Regulator use and leak testing

- Prohibited practices

- Acetylene-specific requirements

- Empty cylinder management

- Emergency procedures for leaks, fires, and cylinder damage

Training shall be provided before initial assignment and refreshed annually or when procedures change.

# 13. Recordkeeping

- Cylinder inventory records (type, quantity, location, supplier)

- Storage area inspection records

- Employee training records

- Incident/near-miss reports involving cylinders

- SDS for all compressed gases on-site

# Appendix A: Compressed Gas Cylinder Inspection Checklist

Inspector Name: _______________________________

Location / Job Site: _______________________________

Date: _______________________________

Individual Cylinder Inspection:

| Item | Cyl. ID / Label | Gas Type | Cap On? | Secured? | Condition | Leak? | In Date? | Pass/Fail |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Inspection Criteria — Check each cylinder for:

- Readable label identifying contents

- Valve protection cap in place (when not in use)

- Cylinder secured upright and stable

- No visible damage (dents, gouges, corrosion, arc strikes, fire damage)

- No leaks (hissing sound, odor, frost formation)

- Hydrostatic test date within acceptable range

- Proper separation of fuel gases and oxidizers

Corrective Actions Taken:

__________________________________________________________________________

__________________________________________________________________________

Inspector Signature: ________________________________________

Date: ________________________________________

# Appendix B: Storage Area Assessment Form

Location / Job Site: _______________________________

Assessed By: _______________________________

Date: _______________________________

Storage Area Compliance Checklist:

| Requirement | Yes | No | N/A | Comments |
| --- | --- | --- | --- | --- |
| Cylinders stored upright and secured |  |  |  |  |
| Valve protection caps in place on stored cylinders |  |  |  |  |
| Fuel gases separated from oxidizers by 20 ft or 5-ft barrier |  |  |  |  |
| Full and empty cylinders separated and labeled |  |  |  |  |
| Storage area well-ventilated |  |  |  |  |
| "No Smoking" signs posted |  |  |  |  |
| Away from electrical circuits and ignition sources |  |  |  |  |
| Protected from weather, direct sunlight, and extreme heat |  |  |  |  |
| Away from elevators, stairs, and egress routes |  |  |  |  |
| Fire extinguisher within 25 feet |  |  |  |  |
| SDS available for all gases stored |  |  |  |  |
| Cylinders protected from vehicle traffic |  |  |  |  |

Corrective Actions Required:

__________________________________________________________________________

__________________________________________________________________________

__________________________________________________________________________

Assessor Signature: ________________________________________

Date: ________________________________________

Corrective Action Completed By: ________________________________________

Date Completed: ________________________________________