## Slide 1
FORBES SAFETY SOLUTIONS
Overhead Power Line Awareness
Ref: 29 CFR 1926.1408 | 29 CFR 1926.416(a)
[Company Name]
[Date]
TOOLBOX TALK

## Slide 2
WHY THIS MATTERS
~60
Workers die annually from power line contact — electrocution is one of OSHA’s Fatal Four
10 ft
Minimum clearance distance from overhead power lines under 50kV for all equipment and workers
53%
Of power line fatalities involve cranes, boom trucks, and aerial lifts making contact

## Slide 3
Clearance Distances & Hazard Recognition
MINIMUM CLEARANCE BY VOLTAGE
Up to 50kV: minimum 10 feet clearance for equipment, loads, and personnel
50kV to 200kV: minimum 15 feet clearance
200kV to 350kV: minimum 20 feet clearance
350kV to 500kV: minimum 25 feet clearance
Over 500kV: 25 ft + 5 ft for each additional 100kV — or as determined by utility
HAZARD RECOGNITION
LOOK UP before you set up — survey every work area for overhead lines
Power lines may sag in hot weather, increasing contact risk
Assume all lines are energized unless the utility confirms de-energization in writing
Electricity can arc — you do NOT have to touch the line for electrocution to occur
Metal ladders, scaffolding, long pipes, and rebar can all conduct electricity

## Slide 4
Equipment Operations & Spotter Requirements
WORKING NEAR POWER LINES
Designate a qualified spotter when operating cranes, boom trucks, or aerial lifts near lines
Spotter must have a clear view of the clearance zone and be in constant communication
Use range-limiting devices or proximity alarms when available
Post warning signs at site entry points identifying overhead hazards
Create a pre-work plan with clearance distances mapped for each overhead line
DE-ENERGIZATION & ALTERNATIVES
Best option: request utility to de-energize and ground the line
If de-energization not possible: insulating barriers or line covers installed by the utility
Use non-conductive tools and equipment when working near energized lines
Barricade the area and establish restricted zones around overhead lines
Maintain minimum distances even for stored materials and equipment staging

## Slide 5
If Equipment Contacts a Power Line
Step | Action | Critical Details
1 | Stay in the cab | The cab and tires provide insulation — you are safest INSIDE the equipment
2 | Warn others | Shout to everyone: stay back at least 35 ft from equipment
3 | Call 911 | Request power company and emergency services immediately
4 | Do NOT exit | Do not step out or touch the ground while touching the equipment
5 | If fire forces exit | Jump clear — both feet together, not stepping out. Do NOT touch equipment and ground simultaneously
6 | Hop away | Keep feet together and hop/shuffle at least 35 ft away to avoid step potential (ground voltage gradient)

## Slide 6
QUIZ / DISCUSSION
1
What is the minimum clearance distance from overhead power lines under 50kV?
Answer: 10 feet for all equipment, loads, and personnel. This distance increases with higher voltage levels.
2
If your equipment contacts a power line, what should you do first?
Answer: Stay inside the cab. The equipment and tires provide insulation. Call 911, warn others to stay back at least 35 feet, and wait for the utility to de-energize the line.
3
If you must exit equipment that has contacted a power line (e.g., due to fire), how do you exit safely?
Answer: Jump clear with both feet together — never step out. Then hop or shuffle with feet together at least 35 feet away to avoid step potential electrocution from the ground voltage gradient.

## Slide 7
ATTENDANCE SIGN-OFF
Overhead Power Line Awareness
# | Print Name | Signature | Company | Date
1 |  |  |  | 
2 |  |  |  | 
3 |  |  |  | 
4 |  |  |  | 
5 |  |  |  | 
6 |  |  |  | 
7 |  |  |  | 
8 |  |  |  | 
9 |  |  |  | 
10 |  |  |  | 
By signing above, I confirm that I attended this toolbox talk and understand the material presented.