FORBES SAFETY SOLUTIONS

JOB HAZARD ANALYSIS

Cable Pulling / Wire Stringing

Regulatory References: 29 CFR 1910.269, 29 CFR 1926 Subpart V, IEEE 524

Document No: FSS-JHA-039  |  Revision: 0  |  Date: _______________

| Project Name: |  | Date: |  |
| --- | --- | --- | --- |
| Location: |  | JHA Number: |  |
| Supervisor: |  | Permit Required: | ☐ Yes ☐ No |
| Prepared By: |  | Reviewed By: |  |

JOB HAZARD ANALYSIS TABLE

| Task Step | Hazard | Risk Level (H/M/L) | Control Measures |
| --- | --- | --- | --- |
| 1. Reel Setup & Pulling Equipment Positioning | Heavy reel handling (tip-over, crush) Equipment struck-by Uneven ground/terrain Traffic near setup area | H M M M | Use mechanical means (forklift, crane) to position reels; never roll by hand on grade Set reel jacks on firm, level ground; chock to prevent movement Verify pulling equipment capacity exceeds maximum pulling tension Establish traffic control for roadside operations per MUTCD Brief crew on pulling plan, communication signals, and emergency stops Position equipment to minimize cable bends and crossing hazards |
| 2. Cable Feeding & Pulling Tension Monitoring | High pulling tension (cable snap/whip) Pinch points at sheaves/rollers Cable abrasion damage Communication failure | H H M M | Set tension limiter on puller per cable manufacturer MSBP specifications Monitor dynamometer continuously; stop if tension exceeds limits Apply approved cable lubricant to reduce friction per IEEE 524 Keep all personnel clear of cable path and behind sheave guards Establish continuous radio communication between reel and puller ends Emergency stop capability at both ends of pull |
| 3. Cable Routing Through Conduit/Duct Bank | Cable jamming Existing cable damage Confined space in manholes Chemical exposure (lubricants) | M H H L | Conduct duct survey (mandrel test) before pulling to verify clear path Identify and protect existing cables in shared duct banks Follow confined space entry procedures for all manhole entries (29 CFR 1910.146) Atmospheric testing before and during manhole operations Use cable guides/rollers at all direction changes to prevent damage Use SDS-approved cable lubricants; provide PPE for chemical handling |
| 4. Splice/Termination Preparation | Electrical contact (adjacent energized cables) Sharp cable edges/cutting tools Chemical exposure (splice materials) Ergonomic strain | H M M M | Verify zero-energy state on cable to be spliced/terminated; use LOTO Identify and maintain safe distance from adjacent energized cables Use proper cable-cutting and stripping tools; cut away from body Follow manufacturer splice/termination procedures exactly Use chemical-resistant gloves when handling splice compounds Provide adequate lighting and ergonomic positioning for workers |
| 5. Testing & Energization Preparation | High-voltage testing (hipot) shock Incorrect cable identification Premature energization | H H H | Clear all personnel from cable route before high-potential testing Post warning signs: 'DANGER - HIGH VOLTAGE TESTING IN PROGRESS' Verify cable phase identification with multiple methods (tone, tag, trace) Ground all cable ends not being tested per IEEE 400 Confirm LOTO clearance before energization steps Notify control center and receive authorization before switching |
| 6. Cleanup & Demobilization | Trip/slip hazards from materials Reel handling injuries Unsecured manhole/vault covers | L M M | Remove all pulling equipment, lubricant containers, and debris Secure all manhole and vault covers flush with grade Verify all cable openings are properly sealed (fire-stop, duct seal) Return reels and equipment using mechanical handling Conduct final site walkthrough for housekeeping Complete as-built documentation and pulling records |

REQUIRED PERSONAL PROTECTIVE EQUIPMENT (PPE)

| ☐ Hard Hat (ANSI Z89.1 Type I, Class E) | ☐ Safety Glasses (ANSI Z87.1) |
| --- | --- |
| ☐ Leather Work Gloves (abrasion-resistant) | ☐ Steel-Toe Boots (ASTM F2413) |
| ☐ High-Visibility Vest (ANSI/ISEA 107 Class 2) | ☐ FR-Rated Clothing (near energized lines) |
| ☐ Hearing Protection (pulling equipment noise) | ☐ Full-Body Harness (if working at height or near openings) |
| ☐ Rubber Insulating Gloves (if near energized conductors) | ☐ Knee Pads (for conduit work) |

EMERGENCY PROCEDURES

1. If cable snaps or whips under tension, all personnel immediately take cover behind solid barriers. Do NOT attempt to grab a cable under tension. Account for all workers.

2. For pinch-point injuries at sheaves or rollers, stop all pulling operations immediately. Administer first aid and call 911 for crush injuries. Do NOT reverse equipment to free trapped limbs without medical guidance.

3. If overhead line contact occurs, assume everything in the work area is energized. Do NOT touch any equipment or cables. Evacuate using shuffle step (feet together). Call utility for emergency de-energization.

4. For manhole/confined space emergencies, do NOT enter for rescue without proper equipment. Activate retrieval system from surface. Call 911 and initiate confined space rescue plan.

5. For heavy reel handling injuries (strain, crush), stop operations and assess injury. Apply RICE protocol for strains. Call 911 for crush or suspected fracture injuries.

6. All incidents require immediate work stoppage, supervisor notification, and incident report within 24 hours.

| Emergency Contact: | 911 / Site-specific: _______________ |
| --- | --- |
| Assembly Point: |  |
| Nearest Hospital: |  |
| First Aid Kit Location: |  |

WORKER SIGN-OFF

By signing below, I acknowledge that I have reviewed and understand this Job Hazard Analysis, the associated hazards, and the required control measures.

| # | Print Name | Signature | Company | Date |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |

REVIEW & APPROVAL

This JHA has been reviewed and approved by the following authorized personnel:

| Role | Name / Signature | Date |
| --- | --- | --- |
| Prepared By (Safety Professional) |  |  |
| Reviewed By (Site Supervisor) |  |  |
| Approved By (Project Manager) |  |  |
| Client Representative (if required) |  |  |

| Next Review Date: |  |
| --- | --- |
| Revision Notes: |  |

FORBES SAFETY SOLUTIONS  |  Committed to Zero Incidents

This document is valid only when all sections are completed and signatures obtained.