FORBES SAFETY SOLUTIONS

JOB HAZARD ANALYSIS

Energized Electrical Work

Regulatory References: NFPA 70E, 29 CFR 1910.331-335, 29 CFR 1926 Subpart K

Document No: FSS-JHA-037  |  Revision: 0  |  Date: _______________

| Project Name: |  | Date: |  |
| --- | --- | --- | --- |
| Location: |  | JHA Number: |  |
| Supervisor: |  | Permit Required: | ☐ Yes ☐ No |
| Prepared By: |  | Reviewed By: |  |

JOB HAZARD ANALYSIS TABLE

| Task Step | Hazard | Risk Level (H/M/L) | Control Measures |
| --- | --- | --- | --- |
| 1. Energized Work Permit & Justification | Unnecessary exposure to electrical hazards Inadequate planning Failure to justify energized work | H H M | Complete Energized Electrical Work Permit (EEWP) per NFPA 70E Document justification: de-energizing creates greater hazard or is infeasible Obtain approval from qualified electrical safety supervisor Perform shock and arc flash risk assessments Brief all workers on specific hazards, boundaries, and emergency plan |
| 2. Approach Boundary Establishment | Unauthorized personnel in danger zone Incorrect boundary distances Arc flash exposure | H H H | Determine Limited, Restricted, and Arc Flash boundaries per NFPA 70E Table 130.4(E)(a) Mark boundaries with barricades, tape, and warning signs Post arc flash labels with incident energy (cal/cm²) on equipment Only qualified persons within Limited Approach Boundary Attendant posted to control access at boundary perimeter |
| 3. Arc Flash PPE Donning | Inadequate PPE rating Improper donning Heat stress from PPE | H M M | Select PPE based on incident energy analysis (cal/cm² rating) Inspect all PPE for damage, cleanliness, and proper rating before use Don arc-rated layers: base layer, coverall/flash suit, hood, gloves, boots Verify all gaps sealed: no exposed skin within arc flash boundary Monitor workers for heat stress; rotate personnel as needed |
| 4. Voltage Testing & Verification | Contact with energized parts Faulty test equipment Incorrect readings | H M H | Use voltage-rated test instruments rated for the voltage present Verify tester operation on known live source BEFORE and AFTER testing (Live-Dead-Live method) Maintain safe approach distances while testing Use insulated tools and one-hand technique Communicate readings clearly to all team members |
| 5. Energized Work Execution | Arc flash (temps to 35,000°F) Arc blast (pressure wave) Electrical shock Burns Secondary blast-force injuries | H H H H H | Only qualified electrical workers perform energized tasks Work one phase/conductor at a time; insulate adjacent conductors Use insulated hand tools rated for voltage Position body to minimize exposure; turn face away from potential arc Maintain minimum approach distance per NFPA 70E Safety watch/attendant present with rescue equipment ready No loose clothing, jewelry, or conductive items |
| 6. Re-establishment of Covers/Barriers | Accidental contact during closeout Unsecured covers Incomplete restoration | H M M | Replace all covers, guards, and barriers before removing PPE Verify all connections are secure and properly torqued Confirm no tools or materials left inside equipment Update arc flash labels if modifications were made Close out Energized Electrical Work Permit Document all work performed and any anomalies found |

REQUIRED PERSONAL PROTECTIVE EQUIPMENT (PPE)

| ☐ Arc-Rated Face Shield / Hood (cal/cm² per hazard analysis) | ☐ Arc-Rated Coveralls or Flash Suit |
| --- | --- |
| ☐ Voltage-Rated Insulating Gloves with Leather Protectors | ☐ Safety Glasses (ANSI Z87.1) under face shield |
| ☐ Dielectric Safety Boots | ☐ Hard Hat (ANSI Z89.1 Type I, Class E) |
| ☐ Hearing Protection (arc blast noise) | ☐ Arc-Rated Balaclava |
| ☐ FR Underwear/Base Layers | ☐ Voltage-Rated Insulating Blankets/Mats |

EMERGENCY PROCEDURES

1. In case of arc flash event, evacuate all personnel from the immediate area. Call 911 immediately. Do NOT attempt to touch the victim until power is confirmed de-energized.

2. For electrical shock, de-energize the circuit from a safe location using insulated tools. Begin CPR/AED if victim is unresponsive. Do NOT move the victim unless in immediate danger.

3. For arc blast injuries (pressure wave), assess for internal injuries, hearing damage, and burns. Treat burns with sterile dressings; do NOT apply ointments or remove fused clothing.

4. If secondary fire occurs from arc flash, use Class C fire extinguisher (CO2 or dry chemical). Evacuate if fire cannot be controlled within 30 seconds.

5. All arc flash incidents require immediate notification to safety department, investigation, and incident report within 24 hours regardless of injury severity.

6. Ensure AED is staged within 2 minutes of the work area. Two qualified first aid/CPR responders must be present.

| Emergency Contact: | 911 / Site-specific: _______________ |
| --- | --- |
| Assembly Point: |  |
| Nearest Hospital: |  |
| First Aid Kit Location: |  |

WORKER SIGN-OFF

By signing below, I acknowledge that I have reviewed and understand this Job Hazard Analysis, the associated hazards, and the required control measures.

| # | Print Name | Signature | Company | Date |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |

REVIEW & APPROVAL

This JHA has been reviewed and approved by the following authorized personnel:

| Role | Name / Signature | Date |
| --- | --- | --- |
| Prepared By (Safety Professional) |  |  |
| Reviewed By (Site Supervisor) |  |  |
| Approved By (Project Manager) |  |  |
| Client Representative (if required) |  |  |

| Next Review Date: |  |
| --- | --- |
| Revision Notes: |  |

FORBES SAFETY SOLUTIONS  |  Committed to Zero Incidents

This document is valid only when all sections are completed and signatures obtained.