FORBES SAFETY SOLUTIONS

JOB HAZARD ANALYSIS

Substation Maintenance

Document No: FSS-JHA-048

Regulatory References: 29 CFR 1910.269, NFPA 70E, NESC (National Electrical Safety Code), IEEE C2

PROJECT INFORMATION

| Project Name: |  | Date: |  |
| --- | --- | --- | --- |
| Location: |  | JHA Number: |  |
| Supervisor: |  | Permit Required: | ☐ Yes ☐ No |
| Work Description: | Substation Maintenance | Revision: | 0 |

JOB HAZARD ANALYSIS

| Task Step | Hazard | Risk Level (H/M/L) | Control Measures |
| --- | --- | --- | --- |
| 1. Switching and Isolation | Arc flash (extreme energy levels) Electrocution during switching operations Induced voltage from adjacent energized equipment | H H H | Follow switching order approved by system operator; wear full arc flash PPE per incident energy study Only qualified switchmen perform operations; verify visible open gap on disconnect switches Maintain Minimum Approach Distance (MAD) per 1910.269 Table R-3; treat adjacent circuits as energized |
| 2. Grounding and Testing | Step and touch potential Electrocution from stored energy (capacitance) Induced voltage on de-energized lines | H H H | Test for absence of voltage with rated equipment; apply temporary protective grounds (TPGs) on all phases Ground all capacitive sources; wait for discharge time; test with hot stick-mounted voltmeter Apply grounds as close to work location as possible; use equipotential zone grounding mat |
| 3. Transformer Inspection/Maintenance | PCB exposure (older equipment) Hot oil burns Fall hazards (climbing transformer) SF6 gas exposure (gas-insulated equipment) | H H M H | Check nameplate for PCB content; if suspect, sample and test per EPA 40 CFR 761; use appropriate PPE and disposal Verify oil temperature before opening; wear heat-resistant gloves; have spill containment in place Use fall protection when climbing; three-point contact on ladders; ensure structural integrity of platforms SF6 is an asphyxiant — monitor oxygen levels; ventilate confined areas; by-products from arcing are toxic (use supplied air for suspected decomposition) |
| 4. Breaker/Relay Testing | Unexpected breaker operation Stored spring energy (mechanism) Electrical contact during testing | H H M | Rack breaker to test position; verify control power isolated; follow manufacturer test procedures Block breaker mechanism before working on springs; wear face shield during spring compression work Use appropriately rated test equipment; maintain clearances; only qualified relay technicians perform testing |
| 5. Bus Work and Connections | Arc flash during connection work Falls from elevated bus structures Induced voltage from parallel conductors | H H H | Verify de-energized and grounded; apply equipotential grounding; wear arc-rated PPE Use aerial lifts or scaffolding with fall protection; 100% tie-off above 4 feet Install temporary protective grounds bracketing work area; use insulated tools |
| 6. Re-Energization | Arc flash during energization Equipment failure on first energization Personnel in restricted area | H H H | Remove all temporary grounds; verify all tools/personnel clear; energize remotely from control room when possible Perform insulation resistance testing before energization; have protection systems in service Complete personnel sweep; verify all LOTO devices removed; obtain authorization from system operator before switching |

REQUIRED PERSONAL PROTECTIVE EQUIPMENT (PPE)

• Arc-rated clothing per NFPA 70E incident energy study (often 40+ cal/cm² for substation work)

• Arc-rated face shield with balaclava (or arc flash suit hood for higher incident energies)

• Voltage-rated gloves (class per voltage level) with leather protectors

• Safety glasses (ANSI Z87.1) under face shield at all times

• Dielectric overshoes or EH-rated safety boots (ASTM F2413)

• Hard hat (ANSI Z89.1 Type I, Class E) — arc-rated for flash hazard areas

• Hearing protection (breaker operation can exceed 85 dB)

• FR-rated high-visibility vest

• Respiratory protection available for SF6/PCB exposure potential

• Fall protection harness (ANSI Z359) for elevated work

ADDITIONAL SAFETY REQUIREMENTS

• All work within substation requires approved switching orders and clearance tags

• Minimum Approach Distances (MAD) per 29 CFR 1910.269 Table R-3 must be maintained at all times

• Two-person rule: minimum two qualified workers present for all substation work

• Ground grid integrity must be verified before any maintenance activities

• Induced voltages from parallel circuits can be lethal — always apply temporary protective grounds

• Wildlife/pest inspection before work — snakes, wasps, and rodents common in substations

• All test equipment must be CAT IV rated for substation environments

EMERGENCY PROCEDURES

• For electrocution: De-energize using emergency trip if safe; do NOT touch victim in contact with energized equipment; call 911; begin CPR/AED if trained and victim is clear of source

• For arc flash: Evacuate area; do NOT remove melted clothing; cool burns with water; call 911; treat for shock

• For SF6 exposure: Move victim to fresh air; administer oxygen if available; call 911; SF6 decomposition products are extremely toxic — do NOT re-enter without SCBA

• For PCB spill: Contain with absorbent; avoid skin contact; notify EPA if spill exceeds 1 lb; document per 40 CFR 761

• Fire response: Use CO2 or dry chemical extinguisher on electrical fires — NEVER water on energized equipment

• Emergency switching procedures posted at: ____________________

• First aid kit, AED, and emergency supplies located at: ____________________

• Nearest hospital/emergency room: ____________________

• Utility dispatch/control room: ____________________

WORKER SIGN-OFF

By signing below, I acknowledge that I have reviewed and understand this Job Hazard Analysis, the associated hazards, and the required control measures for this work activity.

| # | Print Name | Signature | Date | Company/Trade |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |

REVIEW & APPROVAL

| Role | Name / Signature | Date | Next Review Date |
| --- | --- | --- | --- |
| Prepared By |  |  |  |
| Reviewed By |  |  |  |
| Approved By |  |  |  |
| Site Safety Manager |  |  |  |

DISCLAIMER: This JHA is a template provided by Forbes Safety Solutions for general guidance. It must be reviewed, customized, and approved by a qualified safety professional before use on any specific project. Site-specific conditions may require additional hazard controls not listed herein.