FORBES SAFETY SOLUTIONS

JOB HAZARD ANALYSIS

Wind Turbine Maintenance & Inspection

Applicable Standards: 29 CFR 1926 Subpart M (Fall Protection) • 29 CFR 1910.269 (Electric Power Generation) • 29 CFR 1910.147 (LOTO) • NFPA 70E (Arc Flash) • OSHA Wind Energy eTool • ANSI Z359 (Fall Protection Systems) • ANSI/ISEA 121 (Dropped Object Prevention)

PROJECT INFORMATION

| Company Name: |  | Date: |  |
| --- | --- | --- | --- |
| Project/Site: |  | JHA Number: |  |
| Supervisor: |  | Work Activity: |  |
| Turbine ID: |  | Crew Size: |  |

JOB HAZARD ANALYSIS — TASK BREAKDOWN

| TASK STEP | HAZARD | RISK (H/M/L) | CONTROL MEASURES |
| --- | --- | --- | --- |
| 1. Pre-Task Safety Briefing & LOTO Verification | • Failure to identify hazards • Incomplete lockout/tagout • Energized components • Arc flash exposure | H | • Conduct tailboard meeting reviewing scope, hazards, and emergency plan • Verify LOTO per 29 CFR 1910.147 — each worker applies personal lock • Confirm zero-energy state with voltage tester • Review rescue plan and confirm rescue-trained personnel on site • Check weather forecast — abort if winds >35 mph or lightning within 30 miles |
| 2. Climb/Ascent to Nacelle (Ladder or Service Lift) | • Falls from 300+ feet • Cardiac event during climb • Dropped objects • Fatigue/overexertion • Ergonomic strain | H | • 100% tie-off with dual-lanyard system or self-retracting lifeline (SRL) • Use climb-assist system or service elevator where available • Verify anchor points and SRL inspection current • Mandatory rest stops per climb protocol • Tool tethering for all hand tools and equipment • Radio communication maintained at all times • Medical fitness-for-duty certification current |
| 3. Hub Access and Transfer | • Falls during nacelle-to-hub transfer • Confined space conditions in hub • Rotating equipment (blade pitch system) • Pinch points | H | • Verify blade pitch system is locked out before hub entry • Use hub-specific fall protection anchorage • Confined space entry permit if ventilation is inadequate • Atmospheric monitoring (O₂, LEL, CO, H₂S) before entry • Maintain communication with ground crew • Never work alone in hub — minimum two-person team |
| 4. Gearbox / Generator Inspection & Service | • Electrical contact with energized components • Arc flash • Hydraulic fluid under pressure • Rotating equipment • Noise exposure >85 dBA • Slips on oil residue | H | • Verify LOTO on all energy sources (electrical, hydraulic, pneumatic) • Wear arc-rated PPE per NFPA 70E arc flash boundary calculations • Use insulated tools for electrical work • Bleed hydraulic pressure before disconnecting lines • Hearing protection required in nacelle • Clean spills immediately — maintain housekeeping • Follow OEM service manual procedures |
| 5. Blade Inspection / Repair | • Falls from blade or platform • Suspended at height in harness • Lightning strike • High wind gust exposure • Dropped tools/materials • UV/weather exposure | H | • Platform or rope-access crew with SPRAT/IRATA certification • 100% tie-off with twin-leg Y-lanyard or SRL • Lightning 30-30 rule: suspend work if <30 sec between flash and thunder • Wind speed limit: abort exterior blade work at >25 mph sustained • All tools and materials tethered per ANSI/ISEA 121 • Sunscreen, hydration, and shade breaks for outdoor exposure |
| 6. Descent & LOTO Release | • Falls during descent (fatigue) • Premature LOTO removal • Equipment left in nacelle • Incomplete task verification | M | • Controlled descent using climb-assist or service elevator • 100% tie-off maintained until ground level • Systematic LOTO removal — each worker removes own lock • Verify all tools accounted for (tool inventory check) • Supervisor sign-off on completed work before energization • Post-task debrief documenting lessons learned |

FORBES SAFETY SOLUTIONS

PERSONAL PROTECTIVE EQUIPMENT (PPE) REQUIREMENTS

| PPE ITEM | SPECIFICATION / STANDARD | WHEN REQUIRED |
| --- | --- | --- |
| Full Body Harness | ANSI Z359.11 — Class III full body harness with dorsal D-ring | All work at height; donned before ascending tower |
| Twin-Leg SRL / Y-Lanyard | ANSI Z359.14 — self-retracting lifeline, 6 ft. max arrest distance | 100% tie-off during climb, nacelle, hub, and blade work |
| Hard Hat with Chin Strap | ANSI/ISEA Z89.1, Type I, Class E — chin strap rated for at-height use | All times on site and during tower/nacelle operations |
| Arc-Rated Clothing | NFPA 70E — minimum 8 cal/cm² arc rating (or per arc flash study) | Electrical inspection, LOTO verification, generator/switchgear work |
| Dielectric Gloves | ASTM D120 — Class 00 or higher, voltage-rated for task | Any work on or near energized electrical components |
| Safety Glasses / Goggles | ANSI Z87.1 — impact-rated, anti-fog | All maintenance tasks; goggles for grinding/cutting |
| Hearing Protection | ANSI S3.19 — NRR 25+ dB (plugs or muffs) | Inside nacelle during generator operation or when noise >85 dBA |
| Rescue/Descent Device | ANSI Z359.4 — controlled descent device, rated for user + tools | Staged at nacelle; all personnel trained in self-rescue |
| High-Visibility Vest | ANSI/ISEA 107, Class 2 minimum | Ground-level operations and when working near vehicles |
| Tool Lanyards / Tethers | ANSI/ISEA 121 — rated for tool weight | All hand tools and small equipment used at height |

EMERGENCY PROCEDURES & RESCUE PLAN

EMERGENCY PROCEDURES

Rescue Plan: Trained rescue team on site with nacelle rescue kit (descent device, stretcher, trauma bag). Self-rescue and assisted-rescue drills completed within last 12 months.

Fall from Height: Activate rescue team immediately. Do not leave suspended worker hanging >6 minutes (suspension trauma). Use pre-rigged descent system to lower worker to ground.

Medical Emergency at Height: Stabilize worker in nacelle. Contact emergency services and advise of high-angle rescue need. Use service elevator for patient transport if available.

Severe Weather / Lightning: Monitor weather continuously via SCADA and portable weather station. Evacuate nacelle immediately if lightning within 30 miles (30-30 rule) or winds exceed safe threshold.

Fire in Nacelle: Evacuate immediately via controlled descent. Do NOT attempt fire suppression if automatic system fails. Account for all personnel at ground-level muster point.

Emergency Contacts: Site Safety Officer: _____________ ¦ Local EMS: 911 ¦ Nearest Hospital: _____________ ¦ Poison Control: 1-800-222-1222

FORBES SAFETY SOLUTIONS

WORKER ACKNOWLEDGMENT & SIGN-OFF

By signing below, I acknowledge that I have reviewed this JHA, understand the identified hazards and control measures, and agree to follow all safety procedures outlined herein.

| # | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |
| 9 |  |  |  |
| 10 |  |  |  |

JHA REVIEW & APPROVAL

This JHA must be reviewed and approved before work commences. Review is required whenever scope, conditions, or personnel change.

| ROLE | NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| Prepared By (Safety Professional) |  |  |  |
| Reviewed By (Site Supervisor) |  |  |  |
| Approved By (Project Manager) |  |  |  |
| Approved By (HSE Manager) |  |  |  |

REVISION HISTORY

| REV # | DATE | DESCRIPTION | REVISED BY |
| --- | --- | --- | --- |

DISCLAIMER: This JHA template is provided as a guide for safety planning and does not replace site-specific hazard assessments. Employers are responsible for ensuring compliance with all applicable OSHA standards, manufacturer requirements, and company-specific safety programs. This document should be adapted to reflect actual site conditions, equipment, and personnel qualifications.