FORBES SAFETY SOLUTIONS

Electrical Grounding
& Bonding Program

GFCI Protection, AEGCP & Equipment Grounding Requirements

Prepared for:

[COMPANY NAME]

Reference Standards:

29 CFR 1926.404-405 | NFPA 70 (NEC) | NFPA 70E

Date: [DATE]  |  Revision: [REV NUMBER]

# Table of Contents

# 1. Purpose

This Electrical Grounding and Bonding Program establishes requirements for the proper grounding and bonding of electrical equipment and systems at [COMPANY NAME] construction sites and facilities. This program ensures compliance with 29 CFR 1926.404-405, NFPA 70 (National Electrical Code), and NFPA 70E (Standard for Electrical Safety in the Workplace).

Proper grounding and bonding protects employees from electrical shock, electrocution, and fire hazards by providing a low-impedance path for fault currents to safely return to the source and trip protective devices.

# 2. Scope

This program applies to all [COMPANY NAME] construction sites, temporary wiring installations, and operations where portable electric tools, equipment, and extension cords are used. It covers:

- Ground-fault circuit interrupter (GFCI) protection

- Assured Equipment Grounding Conductor Program (AEGCP) as an alternative

- Equipment grounding requirements

- Temporary wiring installations

- Extension cord use and inspection

- Double-insulated tool identification

# 3. Responsibilities

## 3.1 Management

- Provide GFCI-protected outlets or fund the AEGCP

- Ensure adequate electrical testing equipment is available

- Support program enforcement and employee training

## 3.2 Safety Manager / Competent Person

- Develop and maintain this program

- Designate a competent person to implement the AEGCP (if used)

- Conduct or oversee required electrical testing

- Maintain all test logs and inspection records

- Conduct employee training on electrical safety

## 3.3 Designated Competent Person (AEGCP)

Per 29 CFR 1926.404(b)(1)(iii), when the AEGCP is implemented in lieu of GFCIs, a designated competent person shall:

- Implement and oversee the daily testing and inspection program

- Conduct or supervise all required equipment grounding conductor tests

- Maintain written test records and inspection logs

- Remove defective equipment from service immediately

## 3.4 Supervisors

- Ensure GFCI protection is used or AEGCP is in effect before work begins

- Monitor employees for proper cord and equipment use

- Report defective equipment and remove from service

## 3.5 Employees

- Use GFCI-protected outlets for all 120-volt, single-phase, 15- and 20-ampere receptacle outlets on construction sites

- Visually inspect cords and equipment daily before use

- Report defective equipment immediately; do not use

- Never remove or bypass the ground prong on a plug

# 4. Equipment Grounding Requirements

## 4.1 General Requirements

Per 29 CFR 1926.404(f), the following equipment must be grounded:

- All 120-volt, single-phase, 15- and 20-ampere receptacle outlets on construction sites that are not part of the permanent wiring

- All frames of non-current-carrying metal parts of portable and plug-connected equipment

- All cord sets (extension cords) must have an equipment grounding conductor

- Generator frames must be grounded to the system ground unless meeting specific isolation exceptions

## 4.2 Ground-Fault Protection Methods

[COMPANY NAME] shall use one of the following two methods for ground-fault protection on construction sites per 29 CFR 1926.404(b)(1):

Option 1: Ground-Fault Circuit Interrupters (GFCIs)

- All 120-volt, single-phase, 15- and 20-ampere receptacle outlets that are not part of the permanent wiring must be protected by GFCIs

- GFCIs detect imbalances as low as 4–6 milliamps and disconnect power in 1/40th of a second

- GFCI protection may be provided by GFCI-protected receptacles, portable GFCI devices, or GFCI breakers

Option 2: Assured Equipment Grounding Conductor Program (AEGCP)

- An alternative to GFCIs that relies on a rigorous testing and inspection program

- Requires a designated competent person to administer

- See Section 5 for detailed AEGCP requirements

# 5. Assured Equipment Grounding Conductor Program (AEGCP)

When [COMPANY NAME] elects to use the AEGCP as an alternative to GFCI protection per 29 CFR 1926.404(b)(1)(iii), the following requirements apply:

## 5.1 Written Program Requirements

- The AEGCP must be in writing

- The written program must be available on the job site

- A designated competent person must be responsible for the program

- The program must cover all cord sets, receptacles not part of permanent wiring, and equipment connected by cord and plug that are available for use or used by employees

## 5.2 Testing Requirements

The following tests must be performed on all covered equipment and cord sets:

| Test Type | Requirement | Frequency |
| --- | --- | --- |
| Continuity Test | Verify the equipment grounding conductor is electrically continuous from the tool/equipment through the cord to the plug ground prong | Before first use, after repair, and every 3 months |
| Ground Prong Test | Verify the ground prong is present, not bent or broken, and makes proper contact | Before first use, after repair, and every 3 months |
| Terminal Connection Test | Verify proper connections of the equipment grounding conductor at the tool and at all plug/receptacle connections | Before first use, after repair, and every 3 months |

## 5.3 Testing Frequency Summary

- Before first use on a job site

- Before return to use after any repairs

- Before use after any incident that could have caused damage

- At intervals not exceeding 3 months (quarterly)

Note: More frequent testing may be warranted in harsh environments or where damage is likely.

## 5.4 Testing Procedures

- Use a circuit tester or continuity tester approved for the purpose

- Test from the ground pin of the plug to the exposed metal frame of the tool

- Resistance should read near zero ohms (typically <1 ohm for continuity)

- For receptacles: test from the ground slot to the ground bus in the distribution panel

- Record all test results on the AEGCP Test Log (Appendix A)

## 5.5 Color Coding / Identification

Equipment and cord sets that pass testing must be identified by a color-coded marking system:

| Quarter | Period | Color Code |
| --- | --- | --- |
| Q1 | January – March | [COMPANY DESIGNATED COLOR] |
| Q2 | April – June | [COMPANY DESIGNATED COLOR] |
| Q3 | July – September | [COMPANY DESIGNATED COLOR] |
| Q4 | October – December | [COMPANY DESIGNATED COLOR] |

Equipment that has not been tested or has failed testing shall NOT have the current quarter color code applied and shall be removed from service.

# 6. Visual Inspections

In addition to the AEGCP testing, all employees shall perform visual inspections of electrical equipment and cords before each use:

- Check for external defects — fraying, exposed conductors, cut or damaged outer jacket

- Verify ground prong is intact and not bent or missing

- Check plug and connector housing for cracks or damage

- Verify strain relief is intact at both ends

- Check for signs of overheating (discoloration, melting, burning smell)

- Inspect tool housing for cracks that expose internal components

Any cord or equipment failing visual inspection shall be immediately removed from service, tagged "DEFECTIVE — DO NOT USE," and reported to the supervisor.

# 7. Ground Fault Interrupters

When GFCIs are used as the primary protection method:

- Test GFCI devices before each day's use by pressing the "TEST" button to verify the device trips, then pressing "RESET"

- GFCI devices that do not trip during the test shall be removed from service

- Use GFCI protection on all generators used on construction sites for 15- and 20-amp, 120-volt circuits

- Portable GFCI devices must be connected directly to the outlet — not on extension cords downstream

- Replace GFCI devices that show signs of damage or malfunction

# 8. Temporary Wiring

Temporary wiring installations on construction sites shall comply with 29 CFR 1926.405(a):

- Temporary wiring is permitted during construction, remodeling, maintenance, or demolition

- All temporary wiring shall be removed immediately upon completion of the project

- Receptacles shall be of the grounding type and connected to a ground

- Branch circuits must have an equipment grounding conductor

- Temporary lights must be protected by guards unless bulbs are deeply recessed

- Temporary lights must not be suspended by their cords unless designed for that purpose

- Splices in temporary wiring must have insulation equivalent to the cord

- Lamps for general illumination must be protected from contact and breakage

# 9. Extension Cord Requirements

Extension cords (cord sets) used on [COMPANY NAME] job sites must meet the following requirements:

- Three-wire type (hot, neutral, ground) with an equipment grounding conductor

- Listed or labeled by a nationally recognized testing laboratory (UL, CSA, ETL)

- Rated for hard or extra-hard usage (SO, SOW, ST, STW, or equivalent designations)

- Proper wire gauge for the load and length (e.g., 12 AWG minimum for 100-foot runs at 15 amps)

- Must be protected from damage — not run through doorways, windows, or holes unless protected

- Must not be fastened with staples, hung from nails, or suspended by the cord unless designed for it

- Must be used within rated capacity — never daisy-chain multiple extension cords

- Ground prong must NEVER be removed, bent back, or bypassed

# 10. Double-Insulated Tool Identification

Double-insulated tools are an acceptable alternative to equipment grounding per 29 CFR 1926.404(f)(3)(i):

- Double-insulated tools are identified by the "double square" symbol (□ within □) on the tool nameplate

- These tools have two-prong plugs (no ground prong) and do not require grounding

- The outer housing provides a second layer of insulation beyond the normal internal insulation

- Double-insulated tools must still be visually inspected before use

- If the outer housing is cracked or damaged, the tool shall be removed from service — the secondary insulation has been compromised

- Double-insulated tools should not be used in wet conditions without additional GFCI protection

# 11. Training

All employees who use portable electrical tools, equipment, or extension cords shall be trained on:

- Electrical hazards (shock, electrocution, arc flash, fire)

- The purpose and function of equipment grounding

- GFCI operation, testing, and use

- AEGCP requirements (if applicable to the job site)

- Visual inspection procedures for cords and equipment

- Extension cord requirements and limitations

- Identification of double-insulated tools

- Reporting procedures for defective equipment

- Emergency procedures for electrical incidents

Training shall be provided before initial assignment and refreshed annually or when site conditions change.

# 12. Recordkeeping

- AEGCP test logs (retain for duration of project plus 3 years)

- Equipment and cord inspection logs

- GFCI test documentation (daily test records)

- Employee training records

- Records of defective equipment removed from service

# Appendix A: AEGCP Test Log

Job Site / Location: _______________________________

Competent Person: _______________________________

Testing Quarter / Period: _______________________________

Color Code for This Quarter: _______________________________

| Date | Equipment / Cord ID | Description | Continuity OK? | Ground Prong OK? | Connections OK? | Pass/Fail | Color Applied | Tester Initials |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Equipment Failing Test — Corrective Action:

__________________________________________________________________________

__________________________________________________________________________

Competent Person Signature: ________________________________________

Date: ________________________________________

# Appendix B: Extension Cord / Equipment Inspection Log

Job Site / Location: _______________________________

Inspector Name: _______________________________

Date: _______________________________

Daily Visual Inspection Record:

| Date | Cord / Equipment ID | Type | Jacket OK? | Ground Prong? | Plug/Connector OK? | Strain Relief? | Pass/Fail | Inspector |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Items Removed from Service:

| Date | Cord / Equipment ID | Reason Removed | Disposition (Repair/Destroy) | Follow-Up Date |
| --- | --- | --- | --- | --- |

Inspector Signature: ________________________________________

Date: ________________________________________