FORBES SAFETY SOLUTIONS

Portable Fire
Extinguisher Program

Fire Prevention, Extinguisher Maintenance & Employee Training

Prepared for:

[COMPANY NAME]

Reference Standards:

29 CFR 1910.157 | NFPA 10

Date: [DATE]  |  Revision: [REV NUMBER]

# Table of Contents

# 1. Purpose

This Portable Fire Extinguisher Program establishes the requirements for the selection, placement, inspection, maintenance, and employee training associated with portable fire extinguishers at [COMPANY NAME] in compliance with OSHA 29 CFR 1910.157 and NFPA 10: Standard for Portable Fire Extinguishers.

The program ensures that fire extinguishers are properly maintained, accessible, and that employees are trained to respond appropriately to incipient-stage fires.

# 2. Scope

This program applies to all [COMPANY NAME] facilities, job sites, and operations where portable fire extinguishers are provided. It covers:

- All permanent and temporary structures

- Construction job sites

- Maintenance shops and storage facilities

- Company vehicles equipped with fire extinguishers

- Hot work operations

# 3. Responsibilities

## 3.1 Management

- Provide an adequate number and type of fire extinguishers

- Fund inspection, maintenance, and training programs

- Ensure compliance with this program

## 3.2 Safety Manager

- Develop and maintain this program

- Conduct or coordinate annual employee training

- Oversee monthly inspections and annual maintenance

- Contract with certified fire protection service providers

- Maintain all inspection and maintenance records

## 3.3 Supervisors

- Ensure fire extinguishers in their areas are accessible and unobstructed

- Perform or assign monthly visual inspections

- Report any missing, damaged, or discharged extinguishers immediately

## 3.4 Employees

- Know the locations of fire extinguishers in their work areas

- Do not obstruct access to fire extinguishers

- Report missing, damaged, or used fire extinguishers to their supervisor

- Complete required fire extinguisher training

# 4. Fire Classes and Extinguisher Types

## 4.1 Fire Classifications

| Fire Class | Fuel Type | Examples | Extinguisher Type |
| --- | --- | --- | --- |
| Class A | Ordinary combustibles | Wood, paper, cloth, rubber, many plastics | Water, foam, dry chemical, wet chemical |
| Class B | Flammable liquids/gases | Gasoline, oil, grease, paint, propane | CO2, dry chemical, foam, clean agent |
| Class C | Energized electrical | Motors, switchgear, wiring, panels | CO2, dry chemical, clean agent (de-energize first if possible) |
| Class D | Combustible metals | Magnesium, titanium, sodium, lithium | Dry powder (specific to metal type) |
| Class K | Cooking oils/fats | Deep fryers, commercial cooking | Wet chemical (potassium acetate) |

## 4.2 Common Extinguisher Types and Ratings

| Extinguisher Type | Fire Classes | Typical Rating | Effective Range | Discharge Time |
| --- | --- | --- | --- | --- |
| ABC Dry Chemical | A, B, C | 4-A:80-B:C (10 lb) | 10–20 ft | 15–25 sec |
| CO2 (Carbon Dioxide) | B, C | 10-B:C (10 lb) | 3–8 ft | 8–30 sec |
| Water (stored pressure) | A only | 2-A (2.5 gal) | 30–40 ft | 60 sec |
| Class K Wet Chemical | K | Per NFPA 10 | 10–12 ft | 30–85 sec |
| Dry Powder (Class D) | D (specific metals) | Per metal type | 3–8 ft | Varies |
| Clean Agent (Halotron) | A, B, C | 1-A:10-B:C | 6–10 ft | 8–15 sec |

# 5. Placement Requirements

## 5.1 Travel Distance Requirements

Fire extinguishers shall be distributed so that the travel distance for employees to any extinguisher does not exceed the following maximums per 29 CFR 1910.157(d) and NFPA 10:

| Fire Class | Maximum Travel Distance | Maximum Spacing (Approx.) | Minimum Rating |
| --- | --- | --- | --- |
| Class A | 75 feet (22.9 m) | One per 3,000 sq ft (typical) | 2-A minimum |
| Class B | 50 feet (15.2 m) | Based on hazard level | Varies by hazard |
| Class C | Based on Class A or B hazard present | N/A | N/A (rated for A or B) |
| Class D | 75 feet (22.9 m) | Based on work area | Per metal type |
| Class K | 30 feet (9.1 m) | Within kitchen area | Per NFPA 10 |

## 5.2 Mounting Requirements

Per 29 CFR 1910.157(c) and NFPA 10:

- Extinguishers weighing 40 lbs or less: top of extinguisher not more than 5 feet above the floor

- Extinguishers weighing more than 40 lbs: top of extinguisher not more than 3.5 feet above the floor

- Bottom of extinguisher shall be at least 4 inches above the floor

- Extinguishers shall be mounted in conspicuous locations along normal paths of travel

- Locations shall be marked with signage visible from a distance

- Extinguishers shall not be obstructed or obscured from view

## 5.3 Environmental Considerations

- Protect from freezing where temperatures may drop below 40°F (use freeze-rated or antifreeze types)

- Protect from physical damage in high-traffic areas (use cabinets or recessed mounts)

- Corrosive environments may require special coatings or stainless steel units

# 6. Inspection and Maintenance Schedule

## 6.1 Monthly Visual Inspection

A designated person shall visually inspect all fire extinguishers monthly per NFPA 10, Section 7.2. The monthly inspection shall verify:

- Extinguisher is in its designated location

- Access and visibility are not obstructed

- Operating instructions are legible and facing outward

- Tamper seal is intact

- Pressure gauge is in operable range (green zone)

- No visible physical damage, corrosion, or leakage

- Fullness verified by hefting or weighing (CO2 and halogenated types)

Document inspections using the Monthly Inspection Log (Appendix A). Attach the inspection tag to each extinguisher.

## 6.2 Annual Maintenance

All fire extinguishers shall receive a thorough annual maintenance examination by a certified fire protection technician per NFPA 10, Section 7.3. This includes:

- Complete external and internal examination

- Verification of correct agent type and charge

- Mechanical parts examination and lubrication

- Replacement of worn or damaged components

- Recharging if necessary

- New annual maintenance tag applied

## 6.3 Extended Service Intervals

| Service Type | Frequency | Extinguisher Types | Requirements |
| --- | --- | --- | --- |
| 6-Year Maintenance (Internal Exam) | Every 6 years | Stored-pressure types with dry chemical, dry powder, or halogenated agents | Empty, internally examine, recharge |
| 12-Year Hydrostatic Test | Every 12 years | All types requiring hydrostatic testing per NFPA 10 | DOT/TC hydrostatic test of cylinder, recharge |
| 5-Year Hydrostatic Test | Every 5 years | CO2 and stored-pressure water types | Hydrostatic test per DOT requirements |

Extinguishers that fail inspection, maintenance, or hydrostatic testing shall be removed from service, condemned, and replaced.

# 7. Employee Training

## 7.1 General Training Requirements

Per 29 CFR 1910.157(g), where the employer has provided portable fire extinguishers for employee use, the employer shall provide an educational program to familiarize employees with:

- The general principles of fire extinguisher use

- The hazards involved in incipient-stage fire fighting

- Locations of fire extinguishers in their work area

- How to activate the fire alarm and call emergency services

- The PASS technique (Pull, Aim, Squeeze, Sweep)

- When to fight a fire and when to evacuate

## 7.2 Training Frequency

- Initial training: upon hire and upon assignment to a new work area

- Annual refresher: provided at least annually per 29 CFR 1910.157(g)(2)

- Hands-on training: recommended annually, required where employer policy dictates employees may use extinguishers

## 7.3 Hands-On Training Components

- Live fire training with actual extinguisher discharge (or approved simulator)

- Practice with the PASS technique

- Recognition of different extinguisher types and their uses

- Understanding of extinguisher limitations (range, duration, appropriate fire class)

## 7.4 Exemptions from Training

Per 29 CFR 1910.157(g)(4), where the employer has established an emergency action plan and a fire prevention plan that designate certain employees to use fire extinguishers, only those designated employees require training.

If the employer's emergency action plan requires total evacuation and does not permit any employees to use extinguishers, the employer is exempt from the training requirements. However, extinguishers must still be provided and maintained per the standard.

# 8. Fire Prevention Integration

This program integrates with [COMPANY NAME]'s overall fire prevention efforts:

- Hot work operations require a fire watch with a minimum 20-lb ABC extinguisher within 25 feet

- Flammable storage areas shall have appropriate Class B extinguishers within 10 feet of the storage area

- Emergency exit routes shall not be blocked by extinguisher placement

- Fire extinguisher locations shall be incorporated into the site emergency action plan

# 9. Recordkeeping

The following records shall be maintained:

- Monthly inspection logs (retain for minimum 1 year)

- Annual maintenance records (retain for life of extinguisher)

- 6-year and 12-year service records (retain for life of extinguisher)

- Employee training records (retain for duration of employment plus 3 years)

- Extinguisher inventory list (type, location, serial number, manufacture date)

# 10. Program Review

This program shall be reviewed at least annually and updated as needed based on:

- Changes to facilities, processes, or hazard types

- Results of fire incidents or near-misses

- Regulatory changes to OSHA or NFPA standards

- Findings from insurance inspections or fire marshal visits

# Appendix A: Monthly Fire Extinguisher Inspection Log

Building / Job Site: _______________________________

Inspector Name: _______________________________

Month / Year: _______________________________

| Ext. # | Location | Type/Size | Date | Accessible? | Seal Intact? | Gauge OK? | Condition | Initials |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Action Required:

__________________________________________________________________________

__________________________________________________________________________

Inspector Signature: ________________________________________

Date: ________________________________________

# Appendix B: Annual Maintenance Record

Company: _______________________________

Service Provider: _______________________________

Technician Name / Certification #: _______________________________

Date of Service: _______________________________

| Ext. # | Serial # | Type/Size | Mfg Date | Agent Condition | Parts Replaced | Recharged? | Next Service Due | Tech Initials |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Certification:

I certify that the above fire extinguishers have been inspected, maintained, and serviced in accordance with NFPA 10 requirements.

Service Technician Signature: ________________________________________

Certification Number: ________________________________________

Date: ________________________________________

Received By (Company Representative): ________________________________________

Date: ________________________________________